## failure_mechanisms_list (hidden)
Failure Mechanism Cause | Failure Mechanism ID | Local Effect | Subcomponent Affected | Subcomponent_id | Diagnostic test | Weight | asset function | machine type | rotor type | Cooling
Rotor Pole Damage | 1 | Imbalance, increased vibration | Rotor poles | 7 | 6,13 | 7,3 | Generator | Synchronuous | Salient Poles | Air
Stator Winding Insulation deterioration | 2 | Electrical breakdown, overheating | Stator windings, insulation | 2 | 1,2,4,5,11 | 3,1,4,2,2 | Generator | Synchronuous | Salient Poles | Air
Bearing Failure | 3 | Increased vibration, noise | Bearings | 5,6 | 6,13 | 4,6 | Generator | Synchronuous | Salient Poles | Air
Brush Wear | 4 | Sparking, poor commutation | Brushes, commutator | 5,6 | 6 | 10 | Generator | Synchronuous | Salient Poles | Air
Rotor Shaft Misalignment | 5 | Increased vibration, bearing wear | Rotor shaft, bearings | 4 | 6,13 | 4,6 | Generator | Synchronuous | Salient Poles | Air
Cooling System Failure | 6 | Overheating, reduced cooling efficiency | Cooling fans, heat exchangers | 10 | 6 | 10 | Generator | Synchronuous | Salient Poles | Air
Oil Contamination | 7 | Deterioration of lubricating properties | Bearings, gears | 2,11 | 6,13 | 4,6 | Generator | Synchronuous | Salient Poles | Air
Overload winding | 8 | Overheating, insulation breakdown | Windings, insulation | 2,11 | 1,2,4,5,6,11 | 2,1,4,2,1,2 | Generator | Synchronuous | Salient Poles | Air
Grounding Issues | 9 | Potential for electrical shocks | Enclosure | 8 | 6 | 10 | Generator | Synchronuous | Salient Poles | Air
Commutator Issues | 10 | Poor contact, sparking | Commutator segments, brushes | 13 | 6 | 10 | Generator | Synchronuous | Salient Poles | Air
Thermal Cycling Fatigue | 11 | Thermal stresses, material fatigue | Windings, insulation | 2,11 | 1,2,4,5,11 | 3,1,4,2,2 | Generator | Synchronuous | Salient Poles | Air
Erosion and Corrosion | 12 | Surface degradation, reduced lifespan | Metal surfaces, insulation coatings | 2,3,7,8,9,11,13 | 1,2,4,5,6,11 | 1,1,2,3,3,3 | Generator | Synchronuous | Salient Poles | Air
Resonance and Vibration | 13 | Structural damage, increased wear | Structural components, bearings | 2 | 6,9,12 | 4,6,6 | Generator | Synchronuous | Salient Poles | Air
Environmental Factors (Temperature) | 14 | Thermal stress, material degradation | Insulation, cooling system | 10 | 6 | 10 | Generator | Synchronuous | Salient Poles | Air
Phase Imbalance | 15 | Overheating, electrical stress | Windings, insulation | 2 | 1,2,4,6 | 1,1,5,3 | Generator | Synchronuous | Salient Poles | Air
Winding Contamination | 16 | Decrease insulation resistance, reduce cooling | Stator, rotor windings | 2,11 | 1,2,4,5,6,11 | 1,1,2,3,3,3 | Generator | Synchronuous | Salient Poles | Air

## fmdi_rm
feature_1 | feature_2 | feature_3 | feature_4 | feature_5 | feature_6 | feature_7 | feature_8 | feature_9 | feature_10 | feature_11 | feature_12 | feature_13 | feature_14 | feature_15 | failure_mechanism_id | diagnostic_test_id | value
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 1 | 6 | 7
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 1 | 13 | 3
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 2 | 1 | 3
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 2 | 2 | 1
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 2 | 4 | 4
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 2 | 5 | 2
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 2 | 11 | 2
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 3 | 6 | 4
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 3 | 13 | 6
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 4 | 6 | 10
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 5 | 6 | 6
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 5 | 13 | 6
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 6 | 6 | 10
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 7 | 6 | 4
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 7 | 13 | 6
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 8 | 1 | 2
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 8 | 2 | 1
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 8 | 4 | 4
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 8 | 5 | 2
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 8 | 6 | 1
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 8 | 11 | 2
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 9 | 6 | 10
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 10 | 6 | 10
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 11 | 1 | 3
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 11 | 2 | 1
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 11 | 4 | 4
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 11 | 5 | 2
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 11 | 11 | 2
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 12 | 1 | 1
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 12 | 2 | 1
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 12 | 4 | 2
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 12 | 5 | 3
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 12 | 6 | 3
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 12 | 11 | 3
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 13 | 6 | 4
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 13 | 9 | 6
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 13 | 12 | 6
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 14 | 6 | 10
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 15 | 1 | 1
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 15 | 2 | 1
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 15 | 4 | 5
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 15 | 6 | 3
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 16 | 1 | 1
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 16 | 2 | 1
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 16 | 4 | 2
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 16 | 5 | 3
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 16 | 6 | 3
Generator | Synchronuous | Salient Poles | Air | [11 empty] | 16 | 11 | 3
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 1 | 6 | 7
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 1 | 13 | 3
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 2 | 1 | 3
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 2 | 2 | 1
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 2 | 4 | 4
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 2 | 5 | 2
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 2 | 11 | 2
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 3 | 6 | 4
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 3 | 13 | 6
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 4 | 6 | 10
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 5 | 6 | 6
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 5 | 13 | 6
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 6 | 6 | 10
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 7 | 6 | 4
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 7 | 13 | 6
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 8 | 1 | 2
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 8 | 2 | 1
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 8 | 4 | 4
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 8 | 5 | 2
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 8 | 6 | 1
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 8 | 11 | 2
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 9 | 6 | 10
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 10 | 6 | 10
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 11 | 1 | 3
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 11 | 2 | 1
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 11 | 4 | 4
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 11 | 5 | 2
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 11 | 11 | 2
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 12 | 1 | 1
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 12 | 2 | 1
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 12 | 4 | 2
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 12 | 5 | 3
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 12 | 6 | 3
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 12 | 11 | 3
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 13 | 6 | 4
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 13 | 9 | 6
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 13 | 12 | 6
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 14 | 6 | 10
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 15 | 1 | 1
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 15 | 2 | 1
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 15 | 4 | 5
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 15 | 6 | 3
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 16 | 1 | 1
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 16 | 2 | 1
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 16 | 4 | 2
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 16 | 5 | 3
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 16 | 6 | 3
Generator | Synchronuous | Cylindrical | Air | [11 empty] | 16 | 11 | 3
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 1 | 6 | 7
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 1 | 13 | 3
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 2 | 1 | 3
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 2 | 2 | 1
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 2 | 4 | 4
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 2 | 5 | 2
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 2 | 11 | 2
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 3 | 6 | 4
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 3 | 13 | 6
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 4 | 6 | 10
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 5 | 6 | 6
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 5 | 13 | 6
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 6 | 6 | 10
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 7 | 6 | 4
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 7 | 13 | 6
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 8 | 1 | 2
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 8 | 2 | 1
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 8 | 4 | 4
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 8 | 5 | 2
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 8 | 6 | 1
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 8 | 11 | 2
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 9 | 6 | 10
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 10 | 6 | 10
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 11 | 1 | 3
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 11 | 2 | 1
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 11 | 4 | 4
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 11 | 5 | 2
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 11 | 11 | 2
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 12 | 1 | 1
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 12 | 2 | 1
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 12 | 4 | 2
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 12 | 5 | 3
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 12 | 6 | 3
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 12 | 11 | 3
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 13 | 6 | 4
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 13 | 9 | 6
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 13 | 12 | 6
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 14 | 6 | 10
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 15 | 1 | 1
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 15 | 2 | 1
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 15 | 4 | 5
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 15 | 6 | 3
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 16 | 1 | 1
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 16 | 2 | 1
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 16 | 4 | 2
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 16 | 5 | 3
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 16 | 6 | 3
Motor | Synchronuous | Salient Poles | Air | [11 empty] | 16 | 11 | 3
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 1 | 6 | 7
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 1 | 13 | 3
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 2 | 1 | 3
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 2 | 2 | 1
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 2 | 4 | 4
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 2 | 5 | 2
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 2 | 11 | 2
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 3 | 6 | 4
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 3 | 13 | 6
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 4 | 6 | 10
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 5 | 6 | 6
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 5 | 13 | 6
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 6 | 6 | 10
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 7 | 6 | 4
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 7 | 13 | 6
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 8 | 1 | 2
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 8 | 2 | 1
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 8 | 4 | 4
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 8 | 5 | 2
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 8 | 6 | 1
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 8 | 11 | 2
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 9 | 6 | 10
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 10 | 6 | 10
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 11 | 1 | 3
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 11 | 2 | 1
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 11 | 4 | 4
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 11 | 5 | 2
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 11 | 11 | 2
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 12 | 1 | 1
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 12 | 2 | 1
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 12 | 4 | 2
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 12 | 5 | 3
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 12 | 6 | 3
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 12 | 11 | 3
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 13 | 6 | 4
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 13 | 9 | 6
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 13 | 12 | 6
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 14 | 6 | 10
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 15 | 1 | 1
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 15 | 2 | 1
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 15 | 4 | 5
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 15 | 6 | 3
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 16 | 1 | 1
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 16 | 2 | 1
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 16 | 4 | 2
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 16 | 5 | 3
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 16 | 6 | 3
Motor | Synchronuous | Cylindrical | Air | [11 empty] | 16 | 11 | 3
Motor | Asynchronous | Wound Round | Air | [11 empty] | 2 | 1 | 3
Motor | Asynchronous | Wound Round | Air | [11 empty] | 2 | 2 | 1
Motor | Asynchronous | Wound Round | Air | [11 empty] | 2 | 4 | 4
Motor | Asynchronous | Wound Round | Air | [11 empty] | 2 | 5 | 2
Motor | Asynchronous | Wound Round | Air | [11 empty] | 2 | 11 | 2
Motor | Asynchronous | Wound Round | Air | [11 empty] | 3 | 6 | 4
Motor | Asynchronous | Wound Round | Air | [11 empty] | 3 | 13 | 6
Motor | Asynchronous | Wound Round | Air | [11 empty] | 5 | 6 | 6
Motor | Asynchronous | Wound Round | Air | [11 empty] | 5 | 13 | 6
Motor | Asynchronous | Wound Round | Air | [11 empty] | 6 | 6 | 10
Motor | Asynchronous | Wound Round | Air | [11 empty] | 7 | 6 | 4
Motor | Asynchronous | Wound Round | Air | [11 empty] | 7 | 13 | 6
Motor | Asynchronous | Wound Round | Air | [11 empty] | 8 | 1 | 2
Motor | Asynchronous | Wound Round | Air | [11 empty] | 8 | 2 | 1
Motor | Asynchronous | Wound Round | Air | [11 empty] | 8 | 4 | 4
Motor | Asynchronous | Wound Round | Air | [11 empty] | 8 | 5 | 2
Motor | Asynchronous | Wound Round | Air | [11 empty] | 8 | 6 | 1
Motor | Asynchronous | Wound Round | Air | [11 empty] | 8 | 11 | 2
Motor | Asynchronous | Wound Round | Air | [11 empty] | 9 | 6 | 10
Motor | Asynchronous | Wound Round | Air | [11 empty] | 11 | 1 | 3
Motor | Asynchronous | Wound Round | Air | [11 empty] | 11 | 2 | 1
Motor | Asynchronous | Wound Round | Air | [11 empty] | 11 | 4 | 4
Motor | Asynchronous | Wound Round | Air | [11 empty] | 11 | 5 | 2
Motor | Asynchronous | Wound Round | Air | [11 empty] | 11 | 11 | 2
Motor | Asynchronous | Wound Round | Air | [11 empty] | 12 | 1 | 1
Motor | Asynchronous | Wound Round | Air | [11 empty] | 12 | 2 | 1
Motor | Asynchronous | Wound Round | Air | [11 empty] | 12 | 4 | 2
Motor | Asynchronous | Wound Round | Air | [11 empty] | 12 | 5 | 3
Motor | Asynchronous | Wound Round | Air | [11 empty] | 12 | 6 | 3
Motor | Asynchronous | Wound Round | Air | [11 empty] | 12 | 11 | 3
Motor | Asynchronous | Wound Round | Air | [11 empty] | 13 | 6 | 4
Motor | Asynchronous | Wound Round | Air | [11 empty] | 13 | 9 | 6
Motor | Asynchronous | Wound Round | Air | [11 empty] | 13 | 12 | 6
Motor | Asynchronous | Wound Round | Air | [11 empty] | 14 | 6 | 10
Motor | Asynchronous | Wound Round | Air | [11 empty] | 15 | 1 | 1
Motor | Asynchronous | Wound Round | Air | [11 empty] | 15 | 2 | 1
Motor | Asynchronous | Wound Round | Air | [11 empty] | 15 | 4 | 5
Motor | Asynchronous | Wound Round | Air | [11 empty] | 15 | 6 | 3
Motor | Asynchronous | Wound Round | Air | [11 empty] | 16 | 1 | 1
Motor | Asynchronous | Wound Round | Air | [11 empty] | 16 | 2 | 1
Motor | Asynchronous | Wound Round | Air | [11 empty] | 16 | 4 | 2
Motor | Asynchronous | Wound Round | Air | [11 empty] | 16 | 5 | 3
Motor | Asynchronous | Wound Round | Air | [11 empty] | 16 | 6 | 3
Motor | Asynchronous | Wound Round | Air | [11 empty] | 16 | 11 | 3
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 2 | 1 | 3
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 2 | 2 | 1
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 2 | 4 | 4
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 2 | 5 | 2
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 2 | 11 | 2
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 3 | 6 | 4
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 3 | 13 | 6
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 5 | 6 | 6
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 5 | 13 | 6
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 6 | 6 | 10
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 7 | 6 | 4
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 7 | 13 | 6
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 8 | 1 | 2
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 8 | 2 | 1
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 8 | 4 | 4
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 8 | 5 | 2
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 8 | 6 | 1
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 8 | 11 | 2
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 9 | 6 | 10
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 11 | 1 | 3
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 11 | 2 | 1
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 11 | 4 | 4
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 11 | 5 | 2
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 11 | 11 | 2
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 12 | 1 | 1
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 12 | 2 | 1
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 12 | 4 | 2
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 12 | 5 | 3
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 12 | 6 | 3
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 12 | 11 | 3
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 13 | 6 | 4
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 13 | 9 | 6
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 13 | 12 | 6
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 14 | 6 | 10
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 15 | 1 | 1
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 15 | 2 | 1
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 15 | 4 | 5
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 15 | 6 | 3
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 16 | 1 | 1
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 16 | 2 | 1
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 16 | 4 | 2
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 16 | 5 | 3
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 16 | 6 | 3
Motor | Asynchronous | Squirrel cage | Air | [11 empty] | 16 | 11 | 3

## fmdi_cable
feature_1 | feature_2 | feature_3 | feature_4 | feature_5 | feature_6 | feature_7 | feature_8 | feature_9 | feature_10 | feature_11 | feature_12 | feature_13 | feature_14 | feature_15 | name | local effect | failure_mechanism_id | diagnostic_test_id | value
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 15 | 1.5
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 16 | 0.75
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 17 | 2
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 18 | 0.25
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 19 | 4
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 20 | 1.5
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 14 | 2
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 15 | 3
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 16 | 2
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 17 | 3
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 18 | 4.75
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 19 | 0.5
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 20 | 4.75
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 14 | 1
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 15 | 2
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 16 | 1
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 17 | 6
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 14 | 0.5
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 17 | 1.5
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 19 | 2
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 22 | 6
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 14 | 0.5
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 15 | 2
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 16 | 1
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 17 | 4.5
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 18 | 1
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 19 | 1
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Mechanical stress | Increase of mechanical stress | 23 | 14 | 2
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Mechanical stress | Increase of mechanical stress | 23 | 19 | 8
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Mechanical damage | Increase of mechanical stress | 24 | 14 | 3
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Mechanical damage | Increase of mechanical stress | 24 | 19 | 7
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 14 | 0.5
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 15 | 1.5
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 16 | 0.75
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 17 | 2
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 18 | 0.25
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 19 | 3.5
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 20 | 1.5
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Sparking | Floating potential | 26 | 20 | 7
Medium Voltage | XLPE | Bare | Bare | NA | [10 empty] | Sparking | Floating potential | 26 | 22 | 3
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 15 | 1.9
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 16 | 1.15
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 17 | 2.4
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 18 | 0.65
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 19 | 2
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 20 | 1.9
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 14 | 2
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 15 | 3
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 16 | 2
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 17 | 3
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 18 | 4.875
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 19 | 0.25
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 20 | 4.875
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 14 | 1
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 15 | 2
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 16 | 1
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 17 | 6
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 14 | 0.84
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 17 | 1.83
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 19 | 1
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 22 | 6.33
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 14 | 0.6
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 15 | 2.1
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 16 | 1.1
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 17 | 4.6
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 18 | 1.1
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 19 | 0.5
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Mechanical stress | Increase of mechanical stress | 23 | 14 | 2
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Mechanical stress | Increase of mechanical stress | 23 | 19 | 8
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Mechanical damage | Increase of mechanical stress | 24 | 14 | 3
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Mechanical damage | Increase of mechanical stress | 24 | 19 | 7
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 14 | 0.5
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 15 | 1.5
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 16 | 0.75
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 17 | 2
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 18 | 0.25
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 19 | 3.5
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 20 | 1.5
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Sparking | Floating potential | 26 | 20 | 7
Medium Voltage | XLPE | Bare | SSC | NA | [10 empty] | Sparking | Floating potential | 26 | 22 | 3
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 15 | 1.5
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 16 | 0.75
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 17 | 2
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 18 | 0.25
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 19 | 4
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 20 | 1.5
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 14 | 2
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 15 | 3
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 16 | 2
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 17 | 3
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 18 | 4.75
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 19 | 0.5
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 20 | 4.75
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 14 | 1
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 15 | 2
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 16 | 1
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 17 | 6
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 14 | 0.5
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 17 | 1.5
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 19 | 2
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 22 | 6
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 14 | 0.5
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 15 | 2
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 16 | 1
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 17 | 4.5
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 18 | 1
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 19 | 1
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Mechanical stress | Increase of mechanical stress | 23 | 14 | 2
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Mechanical stress | Increase of mechanical stress | 23 | 19 | 8
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Mechanical damage | Increase of mechanical stress | 24 | 14 | 3
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Mechanical damage | Increase of mechanical stress | 24 | 19 | 7
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 14 | 0.5
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 15 | 1.5
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 16 | 0.75
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 17 | 2
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 18 | 0.25
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 19 | 3.5
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 20 | 1.5
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Sparking | Floating potential | 26 | 20 | 7
Medium Voltage | PILC | Bare | Bare | NA | [10 empty] | Sparking | Floating potential | 26 | 22 | 3
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 15 | 1
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 16 | 1
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 19 | 3
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 20 | 5
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 14 | 3
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 15 | 4
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 16 | 3
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 18 | 2
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 19 | 0.5
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 20 | 7.5
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 14 | 1
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 15 | 2
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 16 | 1
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 17 | 0
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 14 | 0
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 21 | 6
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 19 | 1
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 22 | 3
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 14 | 0.5
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 15 | 2
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 16 | 1
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 21 | 3
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 18 | 1.5
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 19 | 2
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Mechanical stress | Increase of mechanical stress | 23 | 14 | 2
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Mechanical stress | Increase of mechanical stress | 23 | 19 | 8
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Mechanical damage | Increase of mechanical stress | 24 | 14 | 3
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Mechanical damage | Increase of mechanical stress | 24 | 19 | 7
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 14 | 0.6
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 15 | 1.4
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 16 | 0.75
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 21 | 2
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 18 | 0.25
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 19 | 3.5
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 20 | 1.5
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Sparking | Floating potential | 26 | 20 | 7
High Voltage | XLPE | Bare | Bare | NA | [10 empty] | Sparking | Floating potential | 26 | 22 | 3
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 15 | 1
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 16 | 1
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 19 | 2
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Contamination - Termination | Increase of leakage current | 17 | 20 | 6
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 14 | 3
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 15 | 4
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 18 | 16 | 3
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 18 | 2
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 19 | 0.25
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 19 | 20 | 7.75
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 14 | 1
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 15 | 2
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 16 | 1
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized contamination - Water Tree | Localised increase of dielectric losses | 20 | 17 | 0
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 14 | 0
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 21 | 6.5
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 19 | 0.5
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 21 | 22 | 3
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 14 | 0.5
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 15 | 2
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 16 | 1
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 21 | 3.5
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 18 | 2
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Dielectric distributed aging | Increase of dielectric losses, reduce of dielectric proprieties | 22 | 19 | 1
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Mechanical stress | Increase of mechanical stress | 23 | 14 | 2
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Mechanical stress | Increase of mechanical stress | 23 | 19 | 8
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Mechanical damage | Increase of mechanical stress | 24 | 14 | 3
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Mechanical damage | Increase of mechanical stress | 24 | 19 | 7
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 14 | 0.6
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 15 | 1.4
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 16 | 0.75
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 21 | 3
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 18 | 0.25
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 19 | 2
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 25 | 20 | 2
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Sparking | Floating potential | 26 | 20 | 7
High Voltage | XLPE | Bare | SSC | NA | [10 empty] | Sparking | Floating potential | 26 | 22 | 3

## fmdi_sw
feature_1 | feature_2 | feature_3 | feature_4 | feature_5 | feature_6 | feature_7 | feature_8 | feature_9 | feature_10 | feature_11 | feature_12 | feature_13 | feature_14 | feature_15 | name | local effect | failure_mechanism_id | diagnostic_test_id | value
Medium Voltage | AIR | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 23 | 1
Medium Voltage | AIR | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 24 | 1.5
Medium Voltage | AIR | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 25 | 0.5
Medium Voltage | AIR | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 26 | 4
Medium Voltage | AIR | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 30 | 3
Medium Voltage | AIR | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 23 | 1
Medium Voltage | AIR | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 24 | 1.5
Medium Voltage | AIR | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 25 | 0.5
Medium Voltage | AIR | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 26 | 4
Medium Voltage | AIR | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 30 | 3
Medium Voltage | AIR | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 30 | 26 | 1.5
Medium Voltage | AIR | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 30 | 28 | 1
Medium Voltage | AIR | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 30 | 30 | 8
Medium Voltage | AIR | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 31 | 26 | 1.5
Medium Voltage | AIR | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 31 | 28 | 1
Medium Voltage | AIR | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 31 | 30 | 8
Medium Voltage | AIR | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 32 | 25 | 3
Medium Voltage | AIR | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 32 | 26 | 1
Medium Voltage | AIR | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 32 | 30 | 6
Medium Voltage | AIR | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 33 | 26 | 4
Medium Voltage | AIR | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 33 | 31 | 6
Medium Voltage | AIR | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 23 | 1
Medium Voltage | AIR | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 24 | 1.5
Medium Voltage | AIR | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 25 | 0.5
Medium Voltage | AIR | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 26 | 4
Medium Voltage | AIR | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 30 | 3
Medium Voltage | AIR | [13 empty] | Mechanical damage | Increase of mechanical stress | 35 | 26 | 10
Medium Voltage | GIS | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 23 | 1.5
Medium Voltage | GIS | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 24 | 2
Medium Voltage | GIS | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 25 | 1
Medium Voltage | GIS | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 26 | 2
Medium Voltage | GIS | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 30 | 3.5
Medium Voltage | GIS | [13 empty] | Gas leakage | Decrease of dielectric proprieties | 28 | 23 | 2.5
Medium Voltage | GIS | [13 empty] | Gas leakage | Decrease of dielectric proprieties | 28 | 24 | 0.5
Medium Voltage | GIS | [13 empty] | Gas leakage | Decrease of dielectric proprieties | 28 | 25 | 1
Medium Voltage | GIS | [13 empty] | Gas leakage | Decrease of dielectric proprieties | 28 | 26 | 4
Medium Voltage | GIS | [13 empty] | Gas leakage | Decrease of dielectric proprieties | 28 | 30 | 2
Medium Voltage | GIS | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 23 | 1.5
Medium Voltage | GIS | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 24 | 2
Medium Voltage | GIS | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 25 | 1
Medium Voltage | GIS | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 26 | 2
Medium Voltage | GIS | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 30 | 3.5
Medium Voltage | GIS | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 30 | 26 | 0.5
Medium Voltage | GIS | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 30 | 28 | 1.5
Medium Voltage | GIS | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 30 | 30 | 8.5
Medium Voltage | GIS | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 31 | 26 | 0.5
Medium Voltage | GIS | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 31 | 28 | 1.5
Medium Voltage | GIS | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 31 | 30 | 8.5
Medium Voltage | GIS | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 32 | 25 | 3.375
Medium Voltage | GIS | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 32 | 26 | 0.25
Medium Voltage | GIS | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 32 | 30 | 6.375
Medium Voltage | GIS | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 33 | 26 | 1
Medium Voltage | GIS | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 33 | 31 | 9
Medium Voltage | GIS | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 23 | 1.5
Medium Voltage | GIS | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 24 | 2
Medium Voltage | GIS | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 25 | 1
Medium Voltage | GIS | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 26 | 2
Medium Voltage | GIS | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 30 | 3.5
Medium Voltage | GIS | [13 empty] | Mechanical damage | Increase of mechanical stress | 35 | 26 | 10
High Voltage | GIS | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 23 | 1.5
High Voltage | GIS | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 24 | 2
High Voltage | GIS | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 25 | 1
High Voltage | GIS | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 26 | 2
High Voltage | GIS | [13 empty] | Contamination | Increase of leakage current, reduce cooling | 27 | 30 | 3.5
High Voltage | GIS | [13 empty] | Gas leakage | Decrease of dielectric proprieties | 28 | 23 | 2.5
High Voltage | GIS | [13 empty] | Gas leakage | Decrease of dielectric proprieties | 28 | 24 | 0.5
High Voltage | GIS | [13 empty] | Gas leakage | Decrease of dielectric proprieties | 28 | 25 | 1
High Voltage | GIS | [13 empty] | Gas leakage | Decrease of dielectric proprieties | 28 | 26 | 4
High Voltage | GIS | [13 empty] | Gas leakage | Decrease of dielectric proprieties | 28 | 30 | 2
High Voltage | GIS | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 23 | 1.5
High Voltage | GIS | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 24 | 2
High Voltage | GIS | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 25 | 1
High Voltage | GIS | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 26 | 2
High Voltage | GIS | [13 empty] | Moisture ingress | Increase of dielectric losses, decrease of dielectric proprieties | 29 | 30 | 3.5
High Voltage | GIS | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 30 | 26 | 0.5
High Voltage | GIS | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 30 | 28 | 1.5
High Voltage | GIS | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 30 | 30 | 8.5
High Voltage | GIS | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 31 | 26 | 0.5
High Voltage | GIS | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 31 | 28 | 1.5
High Voltage | GIS | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 31 | 30 | 8.5
High Voltage | GIS | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 32 | 25 | 3.375
High Voltage | GIS | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 32 | 26 | 0.25
High Voltage | GIS | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 32 | 30 | 6.375
High Voltage | GIS | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 33 | 26 | 1
High Voltage | GIS | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 33 | 31 | 9
High Voltage | GIS | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 23 | 1.5
High Voltage | GIS | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 24 | 2
High Voltage | GIS | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 25 | 1
High Voltage | GIS | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 26 | 2
High Voltage | GIS | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 34 | 30 | 3.5
High Voltage | GIS | [13 empty] | Mechanical damage | Increase of mechanical stress | 35 | 26 | 10

## fmdi_tx
feature_1 | feature_2 | feature_3 | feature_4 | feature_5 | feature_6 | feature_7 | feature_8 | feature_9 | feature_10 | feature_11 | feature_12 | feature_13 | feature_14 | feature_15 | name | local effect | failure_mechanism_id | diagnostic_test_id | value
Distribution | Oil | [13 empty] | Insulation Deterioration | Increase of dielectric losses, decrease of dielectric proprieties | 36 | 32 | 0.5
Distribution | Oil | [13 empty] | Insulation Deterioration | Increase of dielectric losses, decrease of dielectric proprieties | 36 | 33 | 0.5
Distribution | Oil | [13 empty] | Insulation Deterioration | Increase of dielectric losses, decrease of dielectric proprieties | 36 | 37 | 2
Distribution | Oil | [13 empty] | Insulation Deterioration | Increase of dielectric losses, decrease of dielectric proprieties | 36 | 38 | 0.5
Distribution | Oil | [13 empty] | Insulation Deterioration | Increase of dielectric losses, decrease of dielectric proprieties | 36 | 40 | 6
Distribution | Oil | [13 empty] | Insulation Deterioration | Increase of dielectric losses, decrease of dielectric proprieties | 36 | 41 | 0.5
Distribution | Oil | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 37 | 38 | 1
Distribution | Oil | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 37 | 40 | 4
Distribution | Oil | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 37 | 41 | 5
Distribution | Oil | [13 empty] | Winding deformation | Mechanical movement or deformation of windings, core displacement, or shorted turns. | 38 | 35 | 6
Distribution | Oil | [13 empty] | Winding deformation | Mechanical movement or deformation of windings, core displacement, or shorted turns. | 38 | 39 | 1
Distribution | Oil | [13 empty] | Winding deformation | Mechanical movement or deformation of windings, core displacement, or shorted turns. | 38 | 40 | 3
Distribution | Oil | [13 empty] | Core damage | Core insulation breakdown, core movement, or shorted laminations. | 39 | 32 | 5
Distribution | Oil | [13 empty] | Core damage | Core insulation breakdown, core movement, or shorted laminations. | 39 | 39 | 1
Distribution | Oil | [13 empty] | Core damage | Core insulation breakdown, core movement, or shorted laminations. | 39 | 40 | 2
Distribution | Oil | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 40 | 32 | 0.5
Distribution | Oil | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 40 | 33 | 0.5
Distribution | Oil | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 40 | 37 | 3
Distribution | Oil | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 40 | 40 | 6
Distribution | Oil | [13 empty] | Dielectric distributed aging - Thermal againg | Increase of dielectric losses, decrease of dielectric proprieties | 41 | 32 | 0.5
Distribution | Oil | [13 empty] | Dielectric distributed aging - Thermal againg | Increase of dielectric losses, decrease of dielectric proprieties | 41 | 33 | 0.5
Distribution | Oil | [13 empty] | Dielectric distributed aging - Thermal againg | Increase of dielectric losses, decrease of dielectric proprieties | 41 | 37 | 3
Distribution | Oil | [13 empty] | Dielectric distributed aging - Thermal againg | Increase of dielectric losses, decrease of dielectric proprieties | 41 | 40 | 6
Distribution | Oil | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 42 | 37 | 2
Distribution | Oil | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 42 | 40 | 8
Distribution | Oil | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 43 | 39 | 2
Distribution | Oil | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 43 | 40 | 8
Distribution | Oil | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 44 | 37 | 3
Distribution | Oil | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 44 | 40 | 7
Distribution | Oil | [13 empty] | Mechanical stress | Increase of mechanical stress | 46 | 39 | 10
Distribution | Oil | [13 empty] | Mechanical damage | Increase of mechanical stress | 47 | 35 | 8
Distribution | Oil | [13 empty] | Mechanical damage | Increase of mechanical stress | 47 | 39 | 2
Distribution | Dry | [13 empty] | Insulation Deterioration | Increase of dielectric losses, decrease of dielectric proprieties | 36 | 32 | 0.5
Distribution | Dry | [13 empty] | Insulation Deterioration | Increase of dielectric losses, decrease of dielectric proprieties | 36 | 33 | 0.5
Distribution | Dry | [13 empty] | Insulation Deterioration | Increase of dielectric losses, decrease of dielectric proprieties | 36 | 37 | 8
Distribution | Dry | [13 empty] | Insulation Deterioration | Increase of dielectric losses, decrease of dielectric proprieties | 36 | 38 | 0.5
Distribution | Dry | [13 empty] | Insulation Deterioration | Increase of dielectric losses, decrease of dielectric proprieties | 36 | 40 | 0
Distribution | Dry | [13 empty] | Insulation Deterioration | Increase of dielectric losses, decrease of dielectric proprieties | 36 | 41 | 0.5
Distribution | Dry | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 37 | 38 | 3
Distribution | Dry | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 37 | 40 | 0
Distribution | Dry | [13 empty] | Dielectric localized aging - Partial Discharge | Localised aging of the insulation system | 37 | 41 | 7
Distribution | Dry | [13 empty] | Winding deformation | Mechanical movement or deformation of windings, core displacement, or shorted turns. | 38 | 35 | 7
Distribution | Dry | [13 empty] | Winding deformation | Mechanical movement or deformation of windings, core displacement, or shorted turns. | 38 | 39 | 3
Distribution | Dry | [13 empty] | Winding deformation | Mechanical movement or deformation of windings, core displacement, or shorted turns. | 38 | 40 | 0
Distribution | Dry | [13 empty] | Core damage | Core insulation breakdown, core movement, or shorted laminations. | 39 | 32 | 6
Distribution | Dry | [13 empty] | Core damage | Core insulation breakdown, core movement, or shorted laminations. | 39 | 39 | 2
Distribution | Dry | [13 empty] | Core damage | Core insulation breakdown, core movement, or shorted laminations. | 39 | 40 | 0
Distribution | Dry | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 40 | 32 | 2
Distribution | Dry | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 40 | 33 | 2
Distribution | Dry | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 40 | 37 | 6
Distribution | Dry | [13 empty] | Dielectric localized aging - Thermal stress | Localised aging of the insulation system | 40 | 40 | 0
Distribution | Dry | [13 empty] | Dielectric distributed aging - Thermal againg | Increase of dielectric losses, decrease of dielectric proprieties | 41 | 32 | 2
Distribution | Dry | [13 empty] | Dielectric distributed aging - Thermal againg | Increase of dielectric losses, decrease of dielectric proprieties | 41 | 33 | 2
Distribution | Dry | [13 empty] | Dielectric distributed aging - Thermal againg | Increase of dielectric losses, decrease of dielectric proprieties | 41 | 37 | 6
Distribution | Dry | [13 empty] | Dielectric distributed aging - Thermal againg | Increase of dielectric losses, decrease of dielectric proprieties | 41 | 40 | 0
Distribution | Dry | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 42 | 39 | 2
Distribution | Dry | [13 empty] | Sparking | Localised wear of electrical contacts, increase of thermal stress | 42 | 41 | 8
Distribution | Dry | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 43 | 39 | 2
Distribution | Dry | [13 empty] | Arcing | Localised damage of electrical contact, increase of thermal stress | 43 | 41 | 8
Distribution | Dry | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 44 | 37 | 3
Distribution | Dry | [13 empty] | Chemical degradation | Increase of leakage current, decrease of dielectric proprieties | 44 | 39 | 7
Distribution | Dry | [13 empty] | Mechanical stress | Increase of mechanical stress | 46 | 39 | 10
Distribution | Dry | [13 empty] | Mechanical damage | Increase of mechanical stress | 47 | 35 | 8
Distribution | Dry | [13 empty] | Mechanical damage | Increase of mechanical stress | 47 | 39 | 2